## Sheet1
Economic Analysis for Electric Generation
| Electric Generator Rating (total) | 500 | kW
Type of Electric Generator
| Electric Generator Heat Rate | 11200 | BTUs/kWh
| Natural Gas Cost | 0.75 | per therm
Type of Heat Recovery
| Available Recovered Waste Heat | 0
| Percentage of Waste Heat Use | 0%
| Natural Gas Cost | 0.084 | per kWh
| Maintenance Cost | 0.015 | per kWh
| Electric Utility Fixed Costs | 0.01 | per kWh
| Value of Recovered Waste Heat | 0 | per kWh
| Total Cost to Generate Electricity | 0.109 | per kWh
DISCLAIMER: PLEASE NOTE THAT THIS ECONOMIC ANALYSIS IS AN ESTIMATE ONLY BASED ON NUMEROUS CONTINGENCIES AND ASSUMPTIONS. YOUR ACTUAL COSTS AND SAVINGS MAY VARY SIGNIFICANTLY DEPENDING ON USAGE, EQUIPMENT SPECIFICATIONS, LOAD, TARIFF RATE CHANGES, MARKET CONDITIONS, AND OTHER FACTORS THAT ARE SUBJECT TO CHANGE. NEITHER THE SOUTHERN CALIFORNIA GAS COMPANY NOR ANY PERSON ACTING ON ITS BEHALF: (A) MAKES ANY WARRANTY OR REPRESENTATION, EXPRESSED OR IMPLIED, WITH RESPECT TO ACCURACY, COMPLETENESS, OR USEFULNESS OF THE INFORMATION CONTAINED IN THIS REPORT, OR THAT THE USE OF ANY INFORMATION, METHOD OR PROCESS DISCLOSED IN THIS REPORT MAY NOT INFRINGE PRIVATELY OWNED RIGHTS; OR (B) ASSUMES ANY LIABILITIES WITH RESPECT TO USE OF, OR FOR DAMAGE RESULTING FROM THE USE OF, ANY INFORMATION, METHOD, OR PROCESS DISCLOSED IN THIS REPORT.

## Sheet2 (hidden)
| Argument | Type of Electric Generator | Returns
2 | 1 | Rich Burn Engine | 12500
| 2 | Lean Burn Engine | 11200
| 3 | Microturbine | 14700
| 4 | Other | ?????
| Argument | Type of Heat Recovery | Returns | Units | Heat Recovery Value Factor
1 | 1 | None | 0
| 2 | Hot Water | 75 | hp boiler (hot water) | 1
| 3 | Chilled Water | 125 | tons of cooling | 0.65
| 4 | Steam | 60 | hp boiler (steam) | 0.85

## Dialog1 (hidden)
Instructions Fill in all fields in BLUE and make selections from drop-down boxes. For an explanation or help determining input values, click on the help buttons. If you do not fill in a field, a default value is used. Modifying This Spreadsheet Except for the input fields, this spreadsheet is protected (with no password) against modifications. The spreadsheet also contains hidden sheets, dialog boxes, macros, and Visual Basic code. To modify this spreadsheet, unprotect the workbook and unhide all sheets and columns. This analysis tool is provided AS IS and no support will be provided for modifications.
15
Message 2
Message 3

## Dialog2 (hidden)
Rich burn internal combustion engines have excess fuel in the air/fuel mixture and are typically retrofitted with a three-way catalyst and air-fuel ratio controller to control emissions. Lean burn internal combustion engines have excess air in the air/fuel mixture and typically need selective catalytic reduction (such as ammonia injection) to reduce emissions. It is usually not economically feasible to convert a lean burn engine into a rich burn engine or vice versa. If you are unsure of the type of engine, the manufacturer can determine the type of engine based on the model number or serial number from the engine's nameplate. Microturbines are small turbines less than 500 kilowatts provided in packaged units for commercial and industrial use. If the selection of "Other" is chosen, a heat rate in the following row must be specified.
15
Message 2
Message 3

## Dialog3 (hidden)
Selecting a type of generator (rich burn engine, lean burn engine, or microturbine) in the previous field sets the default heat rate in this field. The heat rate of an electric generator is defined as the amount of fuel the generator consumes to produce 1 kWh. Most engine manufacturers provide a heat rate in BTUs/hp-hour (lower heating value) at ISO conditions. To convert the heat rate to net BTUs/kWh (higher heating value), adjustments must be made for the following: Lower to higher heating value Electric generator efficiency Horsepower to kilowatt conversion factor Parasitic loads and transformer losses Adjustments for temperature, altitude, and engine age The default heat rates in this analysis tool are based on average heat rates incorporating the aforementioned adjustments for typical Southern California conditions.
15
Message 2
Message 3

## Dialog4 (hidden)
Enter the total delivered cost of gas per therm including procurement, transportation, and local taxes. This value should represent the "incremental" cost of gas as opposed to the average cost of gas. For more information about gas rates, contact your Account Executive or call (800) GAS-2000. For up-to-date natural gas tariffs, please visit www.socalgas.com. For information on natural gas futures prices, spot market prices, and electricity prices, please visit www.enerfax.com. One therm = 100 cubic feet of gas = 100,000 BTUs
15
Message 2
Message 3

## Dialog5 (hidden)
With additional equipment, heat can be recovered from an engine-generator or microturbine to produce hot water, steam, or chilled water. Choosing a heat recovery option in this field will set an "available" amount of waste heat in the following field. The available waste heat is given in either boiler hp or tons of cooling. This represents the amount of hot water, steam, or chilled water that can be displaced from load on existing equipment.
15
Message 2
Message 3

## Dialog6 (hidden)
The available waste heat is the amount of heat available from the generator whenever the generator is running. However, in some circumstances, not all of the waste heat is used. In this field, enter the estimated percentage of the available waste heat that will actually be used in the process. The following are a few examples: Example 1: The generator runs 12 hours per day with 75 hp of available hot water. All the hot water from a 75 hp boiler is used 6 hours per day. In this example, 50% should be entered in the field. Example 2: The generator runs 24 hours per day all year-round with 100 tons of available chilled water. Chilled water is used for air conditioning 12 hours per day, 6 months per year during the summer. In this example, 25% should be entered in the field. Example 3: The generator runs 24 hours per day all year-round with 80 hp of available steam. A 40 hp steam boiler is used on a regular basis cycling on about 50% of the time. In this example, 25% should be entered in the field. Example 4: The analysis tool shows 100 hp of available hot water, but your system design can produce 120 hp, all of which will be used. In this example, 120% should be entered in the field.
15
Message 2
Message 3

## Dialog7 (hidden)
Enter the estimated maintenance costs per kilowatt-hour. This number is calculated from estimated annual maintenance costs divided by annual kilowatt-hours produced. The following are some guidelines on maintenance costs: Microturbines ~ $0.015/kWh Microturbines with heat recovery ~ $0.02/kWh Engines < 200 kW ~ $0.02/kWh Engines < 200 kW with heat recovery ~ $0.025/kWh Engines 200 kW to 500 kW ~ $0.015/kWh Engines 200 kW to 500 kW with heat recovery ~ $0.02/kWh Engines > 500 kW ~ $0.01/kWh Engines > 500 kW with heat recovery ~ $0.015/kWh
15
Message 2
Message 3

## Dialog8 (hidden)
Electric utility fixed costs represent electricity bill costs that are added on or not reduced as result of generating your own electricity. These costs include applicable standby charges, exit fees, customer charges, demand charges (when generator is down), added facilities charges, and non bypassable surcharges. Although these charges are difficult to estimate, 1 cent per kilowatt-hour is typical.
15
Message 2
Message 3

## Dialog9 (hidden)
This field is in parentheses (a negative number) because it represents a savings as opposed to a cost in generating electricity. The amount represents existing utility costs currently being spent to produce hot water, steam, or chilled water. These utility costs will be eliminated by recovering waste heat from the generator.
15
Message 2
Message 3