Equipment Measure: Steam Trap Replacement

## Measure Description

Steam systems distribute heat from boilers to space heating and process end uses.  All steam distribution systems contain steam traps.

Steam traps are automatic valves used in every steam systems to remove condensate, air and other non-condensable gasses while preventing or minimizing passage of steam.

Failed open steam traps allow steam to escape to drain or to escape to a condensate return system without providing heating service.  This increases the amount of steam that must be generated to meet the heating demand.

There are three major types of steam traps; 1) mechanical, 2) thermostatic, and 3) thermodynamic2.  Float and thermostatic traps are generally used for lower steam pressure systems (ranging from 15 – 125 psig) and will be the most common type traps replaced.  All traps are susceptible to wear and dirt contamination and require periodic monitoring to insure their correct operation.  Faulty (open) steam traps can be diagnosed with ultrasonic, temperature, or conductivity monitoring techniques.

Regular stem trap maintenance and faulty steam trap replacement is important to minimize steam production. This measure provides an incentive for replacement of  faulty steam traps.

## Market Applicability

This measure is applicable for all core gas customers operating steam boilers.  This measure is applicable to buildings with steam space heating systems, laundries, and plants using steam process heating.  The majority of boilers providing heat for these systems operate within the steam pressure range of  75 psig to 125 psig.  Case studies that surveyed plant steam traps found 16% to 18% 3,5,6 of all traps leaking steam. The case studies covered a hospital laundry, a light industrial facility, and a district heating system.

## Terms and Conditions

All replaced steam traps are eligible.    New construction is not eligible.  The location and designation for the replacement steam trap must be provided, along with specification sheet and receipt for the replacement steam trap.

## Cost Effectiveness Modeling Measure Data

Energy savings, installed costs and trap life have been extracted from case studies and are presented below:

Energy Savings Analysis

Case 3 energy savings provides the most realistic energy savings calculation.  It accounts for a large number of  traps with various leakage rates and would be more exemplary of leakage rates experienced in the field than the other cases that require additional assumptions.  An energy loss of 647 Therms per trap per year will be used for the cost effectiveness analysis

Trap Replacement Cost

Replacement trap cost per trap + labor $122 (1)

Measure life

The measure life, of the steam trap, an automatic valve, is 15 years is based on the October 2001 Energy Efficiency Policy Manual for System Controls

References

- “Steam Traps.”Process Heating: www.engr.udayton.edu/udiac/ Documents%5CProcHeat_SteamTrap.doc

- Oland, C.B. “Review of Orifice Plate Steam Trap.” ORNL/TM-2000/353/R1

- “Energy and cost savings through installation of low maintenance steam traps.” Best Practice Programme New Practice Case Study 120 (August 2000): 3,5

- “Steam trap Performance Assessment.” Federal Technology Alerts http://www.pnl.gov/fta/15_steamtrap/15_steamtrap.htm: 7-10

- Griffin, Bob.“The Enbridge Consumers Gas “Steam Saver” Program.” Steam Digest 2001

- “Inspect and Repair Steam Traps.” Energy TIPS Office of Industrial Technologies Energy and Efficiency Renewable Energy. U.S. Department of Energy March 2002