## Combustion Air Preheat
Gas Savings Calculation
Combustion Air Preheat
Parameter |  | Scenario
|  | Baseline | Efficiency Measure | Notes:
Equipment Load and Annual Use Calculation |  |  |  | Verify customer data matches Load Balance Program
1 | Connected load (MBtuh) | 5000 |  | Enter result from Report tab of Load Balance Program
2 | Operating time (hrs/yr) | 7728 |  | Enter result from Report tab of Load Balance Program
3 | Load factor | 0.4 |  | Enter result from Report tab of Load Balance Program
4 | Equivalent full load hours (hrs/yr) | 3091.2 |  | Calc.: (2) operating hours x (3) load factor
5 | Annual gas use (therms/yr) | 154560 |  | Calc: (1) connected load x (4) EFLH / (100 MBtu/therm)
Combustion Air Preheat and Excess Air Assumptions
6 | Flue gas temperature (F) | 2000 | 2000 | Customer Input: Both cases to be set the same
7 | Oxygen (O2) in flue gas (%, dry) | 3 | 3 | Customer Input: Both cases to be set the same
8 | Excess air (%) | 15.5633 | 15.5633 | Calc.: Fitted function of oxygen in flue (7)
9 | Combustion air temperature (F) | 80 | 890 | Customer Input: the basis of the savings
10 | Available Heat to Process (%) | 38.6237 | 57.3449 | Calc.: See workpaper, available heat calculation
Gas Savings Rate and Annual Gas Savings
11 | Gas savings (%) | Base | 32.65% | Calc.:( (10) new - (10) baseline)/(10) new
12 | New Gas Use (therms/year) | Base | 104101.1768 | Calc. (1 - savings % (11)) x baseline gas use (5)
13 | GasSavings (therms/year) |  | 50458.8232 | Calc.: Baseline Gas use (5) - New Gas Use (12)
Annual Dollar Savings
14 | Gas Rate ($/therm) | 0.95 |  | Customer Gas Rate
15 | Annual Savings ($/year) |  | 47935.882 | Calc.: Gas savings (13) x Gas Rate (14)
Source: Calculation methodology provided by Arvind Thekdi, E3M, Inc.
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Hidden Calc Cells rows: 32-37: Available heat calculation
Calc Table: Do Not Delete
| Source: Arvind Thekdi, EC3M | Base | EE Measure
| Stoichiometric Available Heat Calc | 45 | 45
| Excess Air Adjustment | -5.9141 | -5.9141
| Combustion Air Preheat Adjustment | -0.46225 | 18.259
| Final Available Heat Numbers | 38.6237 | 57.3449
Note on D16: Enter as a number and not as a fraction, e.g., 3 and not 0.03 for 3 percent O2 in the flue gas.
Note on D17: Excess air is a function of oxygen in the exhaust. It is calculated here as a polynomial curve fit to the output of an equilibrium combustion model.
Note on D19: Available heat to the furnace equals total gas combustion heat value minus sensible and latent heat in the flue gases. This is a function of the flue gas temperature, the fuel composition, and excess air.
Note on E16: Enter as a number and not as a fraction, e.g., 3 and not 0.03 for 3 percent O2 in the flue gas.
Note on E17: Excess air is a function of oxygen in the exhaust. It is calculated here as a polynomial curve fit to the output of an equilibrium combustion model.
Note on E19: Available heat to the furnace equals total gas combustion heat value minus sensible and latent heat in the flue gases. This is a function of the flue gas temperature, the fuel composition, and excess air.

## Flue gas to air
Gas Savings Calculation
Flue Gas to Air
Flue Gas Heat Recovery for Air Heating |  |  | Notes:
Equipment Load and Annual Use Calculation |  |  | Verify customer data matches Load Balance Program
1 | Connected load (MBtuh) | 2000 | Enter result from Report tab of Load Balance Program
2 | Operating time (hrs/yr) | 4800 | Enter result from Report tab of Load Balance Program
3 | Load factor | 0.32 | Enter result from Report tab of Load Balance Program
4 | Equivalent full load hours (hrs/yr) | 1536 | Calc.: (2) operating hours x (3) load factor
5 | Annual gas use (therms/yr) | 30720 | Calc: (1) connected load x (4) EFLH / (100 MBtu/therm)
Heat Source Process Conditions
6 | Furnace flue gas temp. (F) | 800 | Customer Input: Both cases to be set the same
7 | % O2 in flue gases (dry basis) | 3 | Customer Input: Both cases to be set the same
8 | % Excess air | 15.5633 | Calc.: Fitted function of oxygen in flue (7)
9 | Recoverable heat from flue gases (Therms/year) | 5994.2532 | Calc: Heat contained in flue gases
Air Heater Process Conditions
10 | Air heater - Inlet air temperature (deg. F.) | 60 | Customer Input:
11 | Required air flow for the air heater (scfm) | 1000 | Customer Input:
12 | Expected flue gas/air HX efficiency % | 50 | Customer Input: within appropriate range.
13 | Heat transferred-recovered in air heater (Therms/year) | 2997.1266 | Calc.: (9) x (12)/100
14 | Air temperature at outlet (deg. F.) | 222.6045 | Customer Input: Air temp within appropriate range
Estimated Annual Gas Savings
15 | Combustion efficiency of avoided air heater % | 80 | Customer Input: Efficiency of avoided water heat
16 | Gas Savings (therms/year) | 3746.4083 | Calc.: (13) / ( (15)/100 )
Annual Dollar Savings
17 | Gas Rate ($/therm) | 0.95 | Customer gas rate
18 | Annual Savings ($/year) | 3559.0878 | Calc.: (16) x (17)
Source: Calculation methodology provided by Arvind Thekdi, E3M, Inc.
If you are interested in heating air to a specific-required temperature using the air heater, you should change air flow and/or the expected air heater efficiency until you get the desired air temperature.
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Note on B32: To solve for a desired air temperature use "Tools" "Goal Seek" and set air temperature to the desired value by changing either air flow or HX efficiency.
Note on D16: Enter as a number and not as a fraction, e.g., 3 and not 0.03 for 3 percent O2 in the flue gas.
Note on D17: Excess air is a function of oxygen in the exhaust. It is calculated here as a polynomial curve fit to the output of an equilibrium combustion model.
Note on D18: (One scf of gas plus stoich. combustion air volume plus excess air in scf) x (flue gas temp - ambient temp) x mean specific heat of flue gas x annual gas consumption in therms / heat content of 1 scf natural g
Note on D27: Heat transferred to the air stream divided by the efficiency of the avoided air heater.

## Flue gas to water
Gas Savings Calculation
Flue Gas to Water
Flue Gas Heat Recovery for Water Heating |  |  | Notes:
Equipment Load and Annual Use Calculation |  |  | Verify customer data matches Load Balance Program
1 | Connected load (MBtuh) | 2000 | Enter result from Report tab of Load Balance Program
2 | Operating time (hrs/yr) | 4800 | Enter result from Report tab of Load Balance Program
3 | Load factor | 0.32 | Enter result from Report tab of Load Balance Program
4 | Equivalent full load hours (hrs/yr) | 1536 | Calc.: (2) operating hours x (3) load factor
5 | Annual gas use (therms/yr) | 30720 | Calc: (1) connected load x (4) EFLH / (100 MBtu/therm)
Heat Source Process Conditions
6 | Furnace flue gas temp. (F) | 800 | Customer Input: Both cases to be set the same
7 | % O2 in flue gases (dry basis) | 3 | Customer Input: Both cases to be set the same
8 | % Excess air | 15.5633 | Calc.: Fitted function of oxygen in flue (7)
9 | Recoverable heat from flue gases (Therms/year) | 5994.2532 | Calc: Heat contained in flue gases
Water Heater Process Conditions
10 | Water heater - Inlet water temperature (deg. F.) | 60 | Customer Input:
11 | Required water flow rate (gpm) | 4 | Customer Input:
12 | Expected water/flue gas HX efficiency % | 50 | Customer Input: within appropriate range.
13 | Heat transferred-recovered in water heater (Therms/year) | 2997.1266 | Calc.: (9) x (12)/100
14 | Water temperature at outlet (Deg. F.) | 157.5432 | Calc.:
Estimated Annual Gas Savings
15 | Combustion efficiency of avoided water heater % | 80 | Customer Input: Efficiency of avoided water heat
16 | Gas Savings (therms/year) | 3746.4083 | Calc.: (13) / ( (15)/100 )
Annual Dollar Savings
17 | Gas Rate ($/therm) | 0.95 | Customer gas rate
18 | Annual Savings ($/year) | 3559.0878 | Calc.: (16) x (17)
Source: Calculation methodology provided by Arvind Thekdi, E3M, Inc.
If you are interested in heating air to a specific-required temperature using the air heater, you should change air flow and/or the expected air heater efficiency until you get the desired air temperature.
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Note on B33: To solve for a desired water temperature use "Tools" "Goal Seek" and set water temperature to the desired value by changing either water flow or HX efficiency.

## Water to Water
Gas Savings Calculation
Water to Water Heat Recovery
Hot Water Heat Recovery for Water Heating |  |  | Notes:
Heat Exchanger Inlet Flow Conditions
1 | Hot side water flow rate (lb/hr) | 12000 | User Input
2 | Hot side water inlet temperature (F) | 180 | User Input (keep below the boiling point)
3 | Cold side water flow rate (lb/hr) | 10000 | User Input
4 | Cold side water inlet temperature (F) | 50 | User Input (keep above freezing)
5 | Heat exchanger effectiveness (%) | 70% | User Input, Range is 1-100%, Default is 70%
6 | Heat transfered to cold water (Btuh) | 910000 | Calc: (1 Btu/lb-F) x (5) x [smaller of (1) and (3)] x [(2) - (4)]
7 | Hot water outlet temperature (F) | 104.1667 | Calc: (2) - (6) / (1) / (1 Btu/lb-F)
8 | Cold water outlet temperature (F) | 141 | Calc: (4) + (6) / (3) / (1 Btu/lb-F)
Annual Gas Savings
9 | Operating time (hrs/yr) | 1536 | User Input, 1-8760 hours
10 | Displaced boiler efficiency (%) | 80% | User Input, Range is 1-100%, Default is 80%
11 | Gas Savings (therms/year) | 17472 | Calc: (6) * (9) / (10) / 100000
Annual Cost Savings
12 | Gas Rate ($/therm) | 0.95 | User Input: Customer gas rate
13 | Annual Cost Savings ($/year) | 16598.4 | Calc: (11) x (12)
Source: Calculation methodology provided by EEA, Inc.
If you are interested in heating the secondary water stream to a specific-required temperature, you should change water flow and/or the expected HX effectiveness until you get the desired air temperature.
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Note on B26: To solve for a desired water temperature use "Tools" "Goal Seek" and set water temperature to the desired value by changing either water flow or HX efficiency.
Note on D9: Input: Multiply flow rate in gpm times 500 to get flow rate in lb/hr
Note on D10: Input: Hot water inlet temperature must be significantly greater than cold water inlet temperature but with no steam.
Note on D11: Input: Multiply flow rate in gpm times 500 to get flow rate in lb/hr
Note on D12: Input: Cold water inlet temperature must be significantly less than hot water inlet temperature but above freezing.
Note on D13: Input: Heat exchanger effective is the ratio of the actual heat transfer rate to the maximum possible heat transfer rate, that of an infinitely large counterflow heat exchanger. Default is 70%.
Note on D18: Input: Annual operating time is the scheduled hours of operation of the process.
Note on D19: Input: Thermal efficiency of avoided water heater. Default is 80%.

## Comb. Air. Instructions
Combustion Air Preheat
Equipment Load and Annual Use Calculation – Information from this section is to be taken from the Load Balance Tool. Customer supplied information that varies from the Load Balance Tool requires approval.
1. Input: Equipment rating or connected load (MBtu/hr) is provided by the customer (for screening purposes) this information may be available for customers using the MAS database.
2. Input: Equipment usage rate (hours/year) -- to be taken from the Load Balance Tool
3. Input: Equipment load factor in use (percent ) – to be taken from the Load Balance Tool
4. Calc: Equivalent full load hours = (Line 2) x (Line 3).
5. Calc.: Annual gas consumption = (Line 4) x (Line 1) x MBtu/therm conversion
Flue Gas, Combustion Air, and Excess Air Assumptions
6. Input: Flue gas temperature – a customer supplied input. For combustion air preheat or excess air changes, the before and after flue gas temperatures are to be the same. For direct product heating, the old and new flue gas temperatures will be different. It is assumed that the flue gas temperature will be above 1,000o F. The calculations are not valid for flue gas temperatures below 400o F.
7. Input: Oxygen percent in the flue gas (% dry basis) – a customer supplied input. For combustion air preheat and direct product heating, this value should remain the same. For excess air reduction, the value would be changed.
8. Calc.: Excess air is a function of Oxygen in the exhaust (Line 7). This is function is a polynomial curve fit to the output of a combustion equilibrium model
9. Input: Combustion Air Temperature (degrees F.) – It is assumed that the base case is at ambient conditions. For combustion air preheat, the preheat temperature should be input. In no case should this temperature be higher than the flue gas temperature (Line 6.) For direct product heating, the combustion air temperature is unchanged but the flue gas temperature is reduced (Line 6). For excess air measures, the combustion air temperature remains unchanged.
10. Calc.: Available Heat to the Process (percent) – This is the heart of the calculation and includes the results of three factors: 1) available heat for stoichiometric gas combustion, 2) adjustment for excess air, 3) adjustment for combustion air temperature. (The justification and documentation of this calculation are provided in the Workpaper.)
Gas Savings Rate and Annual Gas Savings
11. Calc.: Gas Savings Percent – (New Available heat – Base Available Heat)/New Available Heat – from line 10. Note: this provides the identical result as (Base gas consumption – new gas consumption)/Base gas consumption.
12. Calc.: New Gas Use = Base Gas Use x (1 – Line 11/100)
13. Calc.: Annual Gas Savings due to efficiency measure – this is the final output of the calculation.
Annual Gas Cost Savings (Optional Calculation)
14. Input: gas rate ($/therm) – Customer gas rate—avoided commodity and delivery rate.
15. Calc.: Annual savings ($/year) – (13) x (14).
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

## Flue to Air Instructions
Flue Gas to Air
Equipment Load and Annual Use Calculation – Information from this section is to be taken from the Load Balance Tool. Customer supplied information that varies from the Load Balance Tool requires approval. These inputs are in the same order and format as for the efficient combustion: combustion air preheat calculator.
1. Input: Equipment rating or connected load (MBtu/hr) is provided by the customer (for screening purposes) this information may be available for customers using the MAS database.
2. Input: Equipment usage rate (hours/year) -- to be taken from the Load Balance Tool
3. Input: Equipment load factor in use (percent ) – to be taken from the Load Balance Tool
4. Calc: Equivalent full load hours = (Line 2) x (Line 3).
5. Calc.: Annual gas consumption = (Line 4) x (Line 1) x MBtu/therm conversion
Heat Source Process Conditions – characterization of the process outlet conditions from which the heat is to be recovered.
6. Input: Flue gas temperature – a customer supplied input.
7. Input: Oxygen percent in the flue gas (% dry basis) – a customer supplied input.
8. Calc.: Excess air is a function of Oxygen in the exhaust (Line 7). This is function is a polynomial curve fit to the output of a combustion equilibrium model.
9. Calc.: Recoverable heat from flue gases (therms/year.) – This is a calculated value that returns the heat content of the flue gases. The calculation is based on the volume, specific heat, and temperature described in the Workpaper.
Air Heater Process Conditions – characterization of the ambient air temperature, air flows, and heat exchanger effectiveness and calculation of heat transferred to the air stream and the outlet air temperature
10. Input: Air heater inlet air temperature (deg. F.) – ambient conditions or somewhat higher due to heat from the blower motor, if applicable, transferred to the air stream.
11. Input: Required air flow for the air heater (scfm) – customer supplied input
12. Input: Expected flue gas/air HX efficiency % -- customer supplied input. The typical range of heat exchanger efficiencies is 25-70%. The calculator warns the user if the input values are out of this typical range.
13. Calc.: Heat transferred-recovered in air heater – equals the recoverable heat in the flue gases multiplied by the heat exchanger efficiency = (9) x (12)/100.
14. Calc.: Air temperature at outlet (deg. F.) – Based on the specific heat of air, the flow rate, and the assumed efficiency of the HX, this line calculates the exit air temperature for use in the secondary process.
Estimated Annual Gas Savings – Calculates an annual gas savings based on an assumed efficiency of an avoided air heater.
15. Input: Combustion efficiency of avoided air heater % -- This variable represents the efficiency of the avoided process that would have been used for air heating.
16. Calc.: -- Gas Savings (therms/year) – the annual gas savings are based on the energy transferred to the air stream divided by the efficiency of the avoided process – (13)/((15/)100).
Annual Gas Cost Savings (Optional Calculation)
17. Input: gas rate ($/therm) – Customer gas rate—avoided commodity and delivery rate.
18. Calc.: Annual savings ($/year) – (16) x (17).
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

## Flue to Water Instructions
Flue Gas to Water
Equipment Load and Annual Use Calculation – Information from this section is to be taken from the Load Balance Tool. Customer supplied information that varies from the Load Balance Tool requires approval. These inputs are in the same order and format as for the efficient combustion: combustion air preheat calculator.
1. Input: Equipment rating or connected load (MBtu/hr) is provided by the customer (for screening purposes) this information may be available for customers using the MAS database.
2. Input: Equipment usage rate (hours/year) -- to be taken from the Load Balance Tool
3. Input: Equipment load factor in use (percent ) – to be taken from the Load Balance Tool
4. Calc: Equivalent full load hours = (Line 2) x (Line 3).
5. Calc.: Annual gas consumption = (Line 4) x (Line 1) x MBtu/therm conversion
Heat Source Process Conditions – characterization of the process outlet conditions from which the heat is to be recovered.
6. Input: Flue gas temperature – a customer supplied input.
7. Input: Oxygen percent in the flue gas (% dry basis) – a customer supplied input.
8. Calc.: Excess air is a function of Oxygen in the exhaust (Line 7). This is function is a polynomial curve fit to the output of a combustion equilibrium model.
9. Calc.: Recoverable heat from flue gases (therms/year.) – This is a calculated value that returns the heat content of the flue gases. The calculation is based on the volume, specific heat, and temperature described in the Workpaper.
Water Heater Process Conditions – characterization of the ambient water temperature, water flow rate, and heat exchanger effectiveness and calculation of heat transferred to the water stream and the outlet water temperature
10. Input: Water heater inlet air temperature (deg. F.) – ambient conditions or average annual groundwater temperature of water.
11. Input: Required water flow for the water heater in gallons per minute (gpm) – customer supplied input
12. Input: Expected flue gas/air HX efficiency % -- customer supplied input. The typical range of heat exchanger efficiencies is 25-70%. The calculator warns the user if the input values are out of this typical range.
13. Calc.: Heat transferred-recovered in water heater – equals the recoverable heat in the flue gases multiplied by the heat exchanger efficiency = (9) x (12)/100.
14. Calc.: Water temperature at outlet (deg. F.) – Based on the specific heat of water[1], the flow rate, and the assumed efficiency of the HX, this line calculates the exit water temperature for use in the secondary process. The calculator warns the user if input values produce a water temperature above 200o F. to avoid the likelihood of producing steam in the heat exchanger.
Estimated Annual Gas Savings – Calculates an annual gas savings based on an assumed efficiency of an avoided air heater.
15. Input: Combustion efficiency of avoided air heater % -- This variable represents the efficiency of the avoided process that would have been used for air heating.
16. Calc.: -- Gas Savings (therms/year) – the annual gas savings are based on the energy transferred to the air stream divided by the efficiency of the avoided process – (13)/((15/)100).
Annual Gas Cost Savings (Optional Calculation)
17. Input: gas rate ($/therm) – Customer gas rate—avoided commodity and delivery rate.
18. Calc.: Annual savings ($/year) – (16) x (17).
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

## W2W Instructions
Water to Water Heat Recovery
The gas savings opportunity being considered here is to use waste heat from hot water to preheat cold water before it enters a boiler. It must be acceptable to drop the temperature of the hot water, such as where the hot water is being sent to a cooling tower. This approach could be effective even when the cold water is not boiler feedwater, but also when the cold water is heated as part of the process. Fouling the heat exchanger is a concern, so water quality is an issue.
Heat Exchanger Inlet Flow Conditions
1. Input: Hot side water flow rate (lb/hr)
If the hot side water flow rate is known in gallons per minute (gpm), multiply the value in gpm times 500 to obtain the value in lb/hr.
2. Input: Hot side water inlet temperature (F)
The hot side water flow is the heat source for the heat exchanger. It must be considerably hotter than the cold side water flow and since this calculator does not handle steam, the hot water must be below its boiling point in the pipe. If the hot water pressure is considerably above atmospheric pressure, the boiling point is considerably above atmospheric pressure. Check a steam table.
3. Input: Cold side water flow rate (lb/hr)
If the cold side water flow rate is known in gallons per minute (gpm), multiply the value in gpm times 500 to obtain the value in lb/hr.
4. Input: Cold side water inlet temperature (F)
The cold side water flow is what is being heated by the heat exchanger. It must be considerably colder than the hot side water flow and must be above the freezing point.
5. Input: Heat exchanger effectiveness (%)
The ideal heat exchanger is an infinitely large counterflow heat exchanger. In it, the inlet stream with the smaller flow will reach the temperature of the other inlet stream. The corresponding amount of heat is the maximum heat that can be exchanged between the two streams. The heat exchanger effectiveness is the ratio of the actual amount of heat received by the cold stream divided by the maximum ideal amount of heat. The default value is 70%, but a more accurate value can be calculated based on the heat exchanger design.
6. Calc: Heat transferred to cold water (Btuh)
Calc: (6) = (1 Btu/lb-F) x (5) x [smaller of (1) and (3)] x [ (2) - (4) ]
7. Calc: Hot water outlet temperature (F)
Calc: (2) - (6) / (1) / (1 Btu/lb-F)
8. Calc: Cold water outlet temperature (F)
Calc: (4) + (6) / (3) / (1 Btu/lb-F)
Annual Gas Savings
9. Input: Operating time (hrs/yr)
Annual scheduled operating time of the process (<= 8760 hours/year)
10. Input: Displaced boiler efficiency (%)
Assuming that the cold water is heated by gas-fired equipment, the heat exchanger reduces the amount of gas burned by that equipment. This value is the thermal efficiency of that gas-fired equipment, most likely a hot-water boiler.
11. Calc: Annual Gas Savings (therms/year)
Calc: (6) * (9) / (10) / 100000
Annual Gas Cost Savings (Optional Calculation)
12. Input: Gas rate ($/therm)
Customer gas rate — avoided commodity and delivery rate
13. Calc: Annual cost savings ($/year)
Calc: (13) = (11) x (12)
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.