QUESTION DRA-DAO-18-1:

SoCalGas’ Baseline Assessment Plan (BAP) for the Transmission Integrity Management Program (TIMP) shows that the primary inspection method used or planned is ILI.  Please answer the following questions regarding the BAP.

  - Please explain why and how ILI was determined to be the best suited inspection method.

  - Please provide a copy of all studies and or assessments/analyses performed by SoCalGas, or on behalf of SoCalGas, to determine that ILI is the method best suited to assess the threats identified for its transmission pipelines.

  - Please identify all advantages and disadvantages of the four methods allowed by the TIMP rule that SoCalGas considered or evaluated in determining the best suited method for pipeline assessment.

RESPONSE DRA-DAO-18-1:

- Pipeline safety regulations allow in-line inspection (ILI), pressure test, direct assessment, and other technology as equivalent options for baseline assessment of transmission pipelines in high consequence areas (HCA).  Each pipeline is evaluated individually, and an approach is selected to complete the assessment.  Several factors impact the selection of the method.  These include pressure and flow of gas, diameter, length of HCA, applicable threats, and time required to complete the assessment. In general, ILI is the preferred choice for assessment at SoCalGas due to the fact that the pipeline systems are conducive to accommodating ILI tools (gas flow, pipeline pressure, diameter, etc), measurements are collected along the entire length of the line, and in general, service impacts to customers are usually manageable.  Lastly, the execution of reassessments every seven years as required by regulations is more practical using ILI compared to other assessment methods.

- Assessment teams evaluate the pipelines in HCA, and select the method to complete the baseline assessment.  Their selection is recorded on the BAP (a copy of which has already been provided to DRA in our General Rate Case).  As projects progress, the assessment method may change due to circumstances such as the ability to obtain permits, vendor availability, and system constraints.

Each method has advantages and limitations, and as such are applicable in different circumstances.  The regulations consider all of the methods to be equivalent for assessment of pipeline integrity.  Section IV.B.2. of our Testimony provides a complete description of the applicable methods for assessment of pipeline condition within the context of the PSEP.   See also ASME Standard “Managing System Integrity of Gas Pipelines,” B31.8S.

QUESTION DRA-DAO-18-2:

Please provide the following for SDG&E’s TIMP.

- Identify the inspection method SDG&E adopted for its TIMP

- Please explain why and how this inspection method was determined to be the best suited for the SDG&E transmission system.

- Please provide a copy of all studies and or assessments/analyses performed by SDG&E, or on behalf of SDG&E, to determine that the method identified in 2(a) above is the method best suited to assess the threats identified for its transmission pipelines.

RESPONSE DRA-DAO-18-2:

- Both ECDA and ILI have been used at SDG&E.

- See Response 1a above.  The same assessment method selection process is used at SDG&E.  ECDA has been selected in several instances due to potential customer impacts associated with the SDG&E system, scheduling requirements, and other pipeline factors.  SDG&E is in the process of retrofitting additional lines for ILI.  ILI technology will be used to perform reassessments (baseline assessments have been completed using ECDA).

- Please refer to Response 1b above.

QUESTION DRA-DAO-18-3:

In response to DRA-DAO-4, questions 1(g) and (h), SoCalGas stated, “All costs for operations and maintenance of pipeline facilities and infrastructure are captured in the appropriate FERC account, as defined in the FERC Uniform System of Accounts.  In addition cost centers are used to help designate the area in which work was completed….”  Please provide the following with regard to this statement:

- The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SoCalGas’ transmission system, for each year from 2001-2011, by FERC account.

- The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SoCalGas’ transmission system, for each year from 2001-2011, by cost centers.

- Provide a mapping of the cost centers in 3(b) to the FERC accounts in 3(a).

- The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SDG&E’s transmission system, for each year from 2001-2011, by FERC account.

- The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SDG&E’s transmission system, for each year from 2001-2011, by cost centers.

- Provide a mapping of the cost centers in 3(d) to the FERC accounts in 3(e).

RESPONSE DRA-DAO-18-3:

Provided below are tables displaying authorized, budgeted and actual (i.e., recorded) operations and maintenance expenses applicable to the 2,960 miles of FERC defined transmission pipeline operated by SoCalGas, and 168 miles operated by SDG&E (Mileage data as 4th Quarter 2011, FERC Form 2).  The years as shown in each table represent that data which was readily available within the internal reporting systems.

Pursuant to a “meet and confer” discussion with DRA, SoCalGas and SDG&E will provide data for 2004 – 2011 as it is readily available.  The Actual data shown in Question 3, Tables 2, 4, 6, and 7 covers the historical period 2004 to 2011.

The data within each of these response tables is presented as it was recorded within each utility’s accounting system (for actual and budget items), or as it was authorized within each applicable regulatory proceeding (for authorized items).  Because certain types of costs are recorded differently between years, and because certain costs are authorized differently between rate cases, data is not directly comparable across tables.   For example, effective 1/1/2005 the Utilities began recording vacation and sick time similar to an overhead charge.  Therefore this type of cost is not forecasted the same in the 2004 Cost of Service (COS) and 2008 General Rate Case (GRC) proceedings.  This impacts not only the comparison between rate proceedings, but also the comparison between actual and authorized values.

Response to (a)

As stated in response to DR-DAO-4, Q1(g):

Therefore, maintenance and inspection costs specific to the 284 miles noted here is not available.   The cost to operate and maintain these segments is recorded along with all other transmission FERC defined costs.

Because of the method of recording costs, Tables 1 and 2 below provide the Authorized and Actual levels of spending for all transmission activities.  “Authorized” costs are the estimates adopted in each of the applicable rate proceedings.

Table 1

Gas Transmission Operations and Maintenance Expense

SoCalGas AUTHORIZED O&M Shown by FERC Account

Direct Nonshared and Direct Shared O&M

SoCalGas’s internal budgeting is performed by cost center.  Therefore the Utility does not have “Budget” figures by FERC account.

“Actual” expense is extracted from SoCalGas’s internal accounting reporting system.  It includes the direct elements of labor, non-labor and other direct offsets to expense.  These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and non-balanced items).   Effective 2005, SCG’s accounting practice was changed to treat vacation/sick time as a loader to each account.  The data below has been adjusted to include this vacation and sick time labor allocation.

Table 2

Gas Transmission Operations and Maintenance Expense

SoCalGas ACTUAL Shown by FERC Account

(Thousand Direct Nominal Dollars, including Vacation & Sick cost allocation)

Response to (b)

The 2004 COS and 2008 GRC costs were authorized by FERC account.  Therefore SoCalGas does not have Authorized amounts by cost center.

“Budgeted” expense displayed in Table 3 below (DRA-DAO 18 Q3b SClGGas Trans Budget.xlsx), are the original operating plan for both shared and non-shared cost centers as extracted from SoCalGas’s internal accounting reporting system.  Because the utilities budget for vacation and sick time as one amount for both Capital and O&M allocations, the Data EXCLUDE any costs related to vacation and sick time.  The cost centers shown have been identified as the key areas responsible for the operations and maintenance of the Transmission lines.  This includes not only cost centers directly within the Transmission field organization, but also cost centers within the Engineering organization that support both transmission and distribution field operations.  These cost centers plan (and charge) to FERC accounts both within and outside the FERC Transmission functional area.   Due to changes in organization structure, the utilization of cost centers has changed over time.

Table 3 (Sample of File Text)

Gas Transmission Operations and Maintenance Expense

SoCalGas Cost Center BUDGET Shown for Transmission Organization

(Thousand Direct Nominal Dollars, O&M activities only;

Excludes Vacation and Sick cost element)

1/  2005 is the last available year for which SoCalGas retains budget information.

“Actual” expense is as extracted from SoCalGas’s internal accounting reporting system.  (Attached file: DRA-DAO-18 Q3 a-f tables-0402.xlsx) These costs include the direct elements of labor, non-labor, other direct offsets to expense, and an allocation of vacation and sick time of various cost centers within the utility operations.   These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items).  This cost center view of “Actual” displays the cost centers and their individual charges to the Transmission FERC accounts.  The totals for Actual spending are the same in Tables 2 and 4.

Table 4 (Sample of File Text)

Gas Transmission Operations and Maintenance Expense

SoCalGas Cost Center ACTUAL Shown for Transmission Organization

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

Response to (c):

The table in the attached excel file (DRA-DAO-18 Q3 a-f tables.xlsx) provide a mapping between the cost center charging and FERC accounting for actual charges 2004 to 2011.

FERC functional accounting represents activities completed.  Utility cost center accounting represents location or workgroup completing various activities. Thus, dependent on the day’s activities, a workgroup will utilize many FERC accounts across various functions to clearly define the activities completed. As shown, the sum across all cost centers for a given FERC account will equal the data shown in Table 2.  However the total sum shown for the cost center is equal to or greater than the data shown in Table 4, since a given cost center will accumulate charges for activities both within and outside a FERC Transmission functional account in their support of the transmission operations (e.g. tools purchase which is charged to a clearing account.)

(Sample of File Text)

Gas Transmission Operations and Maintenance Expense

SoCalGas Cost Center ACTUAL Expenses

By FERC Account and Cost Center Charging

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

Response to (d):

As stated in response to DR-DAO-4, Q1(g):

Therefore, maintenance and inspection costs specific to the 284 miles noted here is not available. The cost to operate and maintain these segments is recorded along with all other transmission FERC defined costs.

Because of the method of recording costs, Tables 5 and 6 below provide the Authorized and Actual levels of spending for all transmission activities.  “Authorized” costs are the amounts adopted in each of the applicable rate proceedings.

Table 5

Gas Transmission Operations and Maintenance Expense

SDG&E AUTHORIZED O&M Shown by FERC Account

Direct Shared and Direct NonShared O&M

SDG&E’s internal budgeting is performed by cost center.  Therefore the Utility does not have “Budget” figures by FERC account.

“Actual” expense is as extracted from SDG&E’s internal accounting reporting system.  It includes the direct elements of labor, non-labor and other direct offsets to expense.  These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items).   Effective 2005, SDGE’s accounting practice was changed to treat vacation/sick time as a loader to each account.  The data below has been adjusted to include this vacation and sick time labor allocation.

Table 6

Gas Transmission Operations and Maintenance Expense

SDG&E ACTUAL Shown by FERC Account

(Thousand Direct Nominal Dollars, including Vacation and Sick cost allocation)

Response to (e)

The 2004 COS and 2008 GRC costs were authorized by FERC account.  Therefore SDG&E does not have Authorized amounts by cost center.

“Budgeted” expense displayed in the table below  are the original operating plan for both shared and non-shared cost centers as extracted from SDG&E’s internal accounting reporting system.  The data EXCLUDE any costs related to vacation and sick time. The utilities budget for vacation and sick time as one amount for both Capital and O&M allocations. The cost centers shown have been identified as the key areas responsible for the operations and maintenance of the Transmission lines.  This includes not only cost centers directly within the Transmission field organization, but also cost centers within the Engineering organization that support both transmission and distribution field operations.  These cost centers plan (and charge) to FERC accounts both within and outside the FERC Transmission functional area.   Due to changes in organization structure, the utilization of cost centers may have changed over time.

Gas Transmission Operations and Maintenance Expense

SDG&E Cost Center BUDGET Shown for Transmission Organization 1/

(Thousand Direct Nominal Dollars, O&M activities only;

Excludes Vacation and Sick cost element)

1/  “Budget” data is maintained within the accounting system only back to 2005.

“Actual” spending by cost center on distribution activities was provided previously with responses to DRA-DAO-18 Q3a-f.

The 2004 COS and 2008 GRC costs were authorized by FERC account.  Therefore SDG&E does not have Authorized amounts by cost center.

“Budgeted” expense for SDG&E Transmission will be provided in a subsequent response in format similar to that provided for SoCalGas in response to 3b, Table 3.

“Actual” expense is as extracted from SDG&E’s internal accounting reporting system.  (Attached file: DRA-DAO-18 Q3 a-f tables.xlsx) These costs include the direct elements of labor, non-labor, other direct offsets to expense, and an allocation of vacation and sick time of various cost centers within the utility operations.    These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items).   This cost center view of “Actual” displays the cost centers and their individual charges to the Transmission FERC accounts.  The totals for Actual spending are the same in Tables 6 and 7.

Table 7 (Sample File Text)

Gas Transmission Operations and Maintenance Expense

SDG&E Cost Center ACTUAL Shown for Transmission Organization

(Direct Nominal Dollars, including Vacation and Sick cost allocation)

Response to (f)

The table in the attached excel file (DRA-DAO-18 Q3 a-f tables.xlsx) provide a mapping between the cost center charging and FERC accounting for actual charges 2004 to 2011.

FERC functional accounting represents activities completed.  Utility cost center accounting represents location or workgroup completing various activities. Thus, dependent on the day’s activities, a workgroup will utilize many FERC accounts across various functions to clearly define the activities completed.  As shown, the sum across all cost centers for a given FERC account will equal the data shown in Table 6.  However the total sum shown for the cost center is equal to or greater than the data shown in Table 7, since a given cost center will accumulate charges for activities both within and outside a FERC Transmission functional account in their support of the transmission operations.

(Sample of File Text)

Gas Transmission Operations and Maintenance Expense

SDG&E Cost Center ACTUAL Expenses

By FERC Account and Cost Center Charging

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

ATTACHMENTS:

QUESTION DRA-DAO-18-4:

Please provide the following for SoCalGas’ and SDG&E’s distribution system:

  - The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SoCalGas’ distribution system, for each year from 2001-2011, by FERC account.

  - The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SoCalGas’ distribution system, for each year from 2001-2011, by cost centers.

  - Provide a mapping of the cost centers identified in 4(a) to the FERC accounts identified in 4(c).

  - The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SDG&E’s distribution system, for each year from 2001-2011, by FERC account.

  - The authorized, budgeted, and actual costs of operations and maintenance of pipeline facilities and infrastructure, including leak surveys and any and all inspection activities performed on SDG&E’s distribution system, for each year from 2001-2011, by cost centers.

  - Provide a mapping of the cost centers identified in 4 (d) to the FERC accounts identified in 4(e).

RESPONSE DAO-18-4:

Pursuant to a “meet and confer” discussion with DRA, SoCalGas and SDG&E understand that the term “Distribution” as used in this question is to reference those lines classified for FERC accounting/reporting as Distribution, but categorized by the DOT definitions as Transmission.

SoCalGas and SDG&E utilize FERC functional reporting to classify and record costs related to its pipeline system.  There is no further distinction by DOT definitions in the accounting for the operations and maintenance cost of these lines.   Therefore the cost for operations and maintenance of these select pipelines is integrated in the total Distribution expense level.

Provided below are tables displaying authorized, budgeted and actual (i.e., recorded)

operations and maintenance expenses applicable to the estimated 49,688 miles of FERC defined distribution pipelines operated by SoCalGas, and 8,494 miles operated by SDG&E (Mileage data as 4th quarter 2011).  The years as shown in each table represent that data which was readily available within the internal reporting systems.

Also pursuant to the “meet and confer” discussion, the utilities will provide data for 2004 – 2011 as it is readily available.  The Actual data shown in Question 3, Tables 2, 4, 6, and 8 covers the historical period 2004 to 2011.

The data within each of these response tables is presented as it was recorded within each utility’s accounting system (for actual and budget items), or as it was authorized within each applicable regulatory proceeding (for authorized items).  Because certain types of costs are recorded differently between years, and because certain costs are authorized differently between rate cases, data is not directly comparable across tables.   For example, effective 1/1/2005 the Utilities began recording vacation and sick time similar to an overhead charge.  Therefore this type of cost is not forecasted the same in the 2004 Cost of Service (COS) and 2008 General Rate Case (GRC) proceedings.  This impacts not only the comparison between rate proceedings, but also the comparison between actual and authorized values.

Response to (a)

Because of the method of recording costs, Tables 1 and 2 below provide the Authorized and Actual levels of spending for all distribution activities.  Note, “Authorized” expenses are the levels as displayed in each of the applicable rate proceedings.  Effective 1/1/2005 the Utilities began treating vacation and sick time similar to an overhead charge.  Thus this type of cost is not treated the same in the 2004 COS and 2008 GRC proceedings.  This impacts not only the comparative between rate proceedings, but also between actual and authorized values.

Table 1

Gas Distribution Operations and Maintenance Expense

SoCalGas AUTHORIZED Levels Shown by FERC Account

Direct Nonshared and Direct Shared O&M

SoCalGas’s internal budgeting is performed by cost center.  Therefore the Utility does not have “Budget” figures by FERC account.

“Actual” expense is extracted from SoCalGas’s internal accounting reporting system.  It includes the direct elements of labor, non-labor and other direct offsets to expense.  These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items).   Effective 2005, SoCalGas’s accounting practice was changed to treat vacation/sick time as a loader to each account.  The data below has been adjusted to include this vacation and sick time labor allocation.

Table 2

Gas Distribution Operations and Maintenance Expense 1/

SoCalGas ACTUAL Shown by FERC Account

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

1/  Includes charges for Distribution Integrity Management Program (which were approved in TY2008 GRC as refundable program).

Response to (b)

The 2004 COS and 2008 GRC costs were authorized by FERC account.  Therefore SoCalGas does not have Authorized amounts by cost center.

“Budgeted” expense displayed in Table 3 below (DRA-DAO-18 Q4b SCG Gas Dist Budget.xlsx), are the original operating plan for both shared and non-shared cost centers as extracted from SoCalGas’s internal accounting reporting system.  Because the utilities budget for vacation and sick time as one amount for both Capital and O&M allocations, the Data EXCLUDE any costs related to vacation and sick time.  The cost centers shown have been identified as the key areas responsible for the operations and maintenance of the Distribution lines.  These cost centers plan (and charge) to FERC accounts both within and outside the FERC Distribution functional area.   Due to changes in organization structure, the utilization of cost centers has changed over time.

Table 3 (Sample of Text File)

Gas Distribution Operations and Maintenance Expense

SoCalGas BUDGETED Expenses by Relevant Cost Centers

SoCalGas Cost Center BUDGET Shown for Distribution Field Organizations 1/

(Thousand Direct Nominal Dollars, excludes Vacation and Sick cost element)

1/ Includes selected cost centers from the entire Distribution organization representing the field operations that is generally responsible for completing the operations and maintenance activities.

2/  SoCalGas only retains budget information within the accounting system back to 2005.

“Actual” expense is as extracted from SoCalGas’s internal accounting reporting system.  (Attached file:  DRA-DAO-18 Q4a-f tables.xlsx) These costs include the direct elements of labor, non-labor, other direct offsets to expense, and an allocation of vacation and sick time of various cost centers within the utility operations.   These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items). This cost center view of “Actual” displays the cost centers and their individual charges to the Distribution FERC accounts.  The totals for Actual spending are the same in Tables 2 and 4.

Table 4 (Sample of Text file)

Gas Distribution Operations and Maintenance Expense

SoCalGas Cost Center ACTUAL Shown for Distribution Organization

(Thousand Direct Nominal Dollars, includes Vacation and Sick cost allocation)

Response to (c):

The table in the attached excel file (DRA-DAO-18 Q4a-f tables.xlsx) provide a mapping between the cost center charging and FERC accounting for actual charges 2005 to 2011.

FERC functional accounting represents activities completed.  Utility cost center accounting represents location or workgroup completing various activities. Thus, depending on the  activities, a workgroup will utilize many FERC accounts across various functions to clearly define the activities completed.  As shown, the sum across all cost centers for a given FERC account will equal the data shown in Table 2.  However the total sum shown for the cost center is equal to or greater than the data shown in Table 4, since a given cost center will accumulate charges for activities both within and outside a FERC Distribution functional account in their support of the distribution operations (e.g.tools purchases which is recorded to a clearing account.)

(Sample of File Text)

Gas Distribution Operations and Maintenance Expense

SoCalGas Cost Center ACTUAL Expenses

By FERC Account and Cost Center Charging

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

Response to (d):

Because of the method of recording costs, Tables 5 and 6 below provide the Authorized and Actual levels of spending for all distribution activities.  “Authorized” expenses are the amounts adopted in each of the applicable rate proceedings.

Table 5

Gas Distribution Operations and Maintenance Expense

SDG&E AUTHORIZED O&M Shown by FERC Account

Direct Nonshared and Direct Shared O&M

.

SDG&E’s internal budgeting is performed by cost center.  Therefore the Utility does not have “Budget” figures by FERC account.

“Actual” expense is as extracted from SDG&E’s internal accounting reporting system.  It includes the direct elements of labor, non-labor and other direct offsets to expense.   These are reported at 100% incurred levels, and reflect all utility spending (i.e. balanced and nonbalanced items).  Effective 2005, SDG&E’s accounting practice was changed to treat vacation/sick time as a loader to each account.  The data below has been adjusted to include this vacation and sick time labor allocation.

Table 6

Gas Distribution Operations and Maintenance Expense

SDG&E ACTUAL Shown by FERC Account

(Thousand Direct Nominal Dollars, including Vacation and Sick cost allocation)

Response to (e)

The 2004 COS and 2008 GRC costs were authorized by FERC account.  Therefore SDG&E does not have Authorized amounts by cost center.

“Budgeted” expense in the excel attachment “DRA-DAO-18 Q4e SDGE Gas Dist Budget.xls”, are the original operating plan for both shared and non-shared cost centers as extracted from SDG&E’s internal accounting reporting system.  Because the utilities budget for vacation and sick time as one amount for both Capital and O&M allocations, the Data EXCLUDE any costs related to vacation and sick time.  The cost centers shown have been identified as the key areas responsible for the operations and maintenance of the Distribution lines.  These cost centers plan (and charge) to FERC accounts both within and outside the FERC Distribution functional area.   Due to changes in organization structure, the utilization of cost centers may have changed over time.

Gas Distribution Operations and Maintenance Expense

SDG&E Cost Center BUDGET Shown for Distribution Field Organizations 1/

(Thousand Direct Nominal Dollars, excludes Vacation and Sick cost element)

(Sample of File Text –Complete Table in the excel attachment below)

1/  “Budget” data is maintained within the accounting system only back to 2005.

“Actual” spending by cost center on distribution activities was provided previously with responses to DRA-DAO-18 Q4a-f.

ATTACHMENT:

Response to (f)

The table in the attached excel file (DRA-DAO-18 Q4a-f tables.xlsx) provide a mapping between the cost center charging and FERC accounting for actual charges 2005 to 2011.

FERC functional accounting represents activities completed.  Utility cost center accounting represents location or workgroup completing various activities. Thus, depending on the activities, a workgroup will utilize many FERC accounts across various functions to clearly define the activities completed.  As shown, the sum across all cost centers for a given FERC account will equal the data shown in Table 6.  However the total sum shown for the cost center is equal to or greater than the data shown in Table 8, since a given cost center will accumulate charges for activities both within and outside a FERC Distribution functional account in their support of the distribution operations.

(Sample of File Text)

Gas Distribution Operations and Maintenance Expense

SDG&E Cost Center ACTUAL Expenses

By FERC Account and Cost Center Charging

(Direct Nominal Dollars, includes Vacation and Sick cost allocation)

ATTACHMENTS:

QUESTION DRA-DAO-18-05:

Provide the following for SoCalGas’ and SDG&E’s transmission pipelines, for each year from 2001-2011:

- The number of miles inspected.

- The number of repairs made.

- The expense incurred for inspection.

- The expense incurred for repairs.

- The number of miles of pipelines replaced.

- The cost incurred for pipeline replacement.

- A breakdown of the replacement cost of the lines replaced by segment, diameter, and pipeline material.

Response DRA-DAO-18-05:

For purposes of preparing these responses, “transmission pipelines” is construed to refer to the United States Department of Transportation (DOT) defined transmission pipelines operated by SoCalGas and SDG&E’s Gas Transmission Operations organizations.

The Transmission Integrity Management Program was initiated in 2002 pursuant to federal regulations, with work commencing in 2003.  Because the program did not start until 2003, responsive data on work elements and costs is not readily available before that time.  While no formalized TIMP-like inspection program was in place prior to 2003, SoCalGas and SDG&E have performed maintenance/inspection activities to validate the integrity of the transmission pipelines, including leak surveys, pipeline patrols, damage prevention programs and corrosion control measures, among others.  In addition, whenever pipeline segments are exposed, their condition and attributes are examined and recorded and any required remedial actions are addressed.

- To complete the inspection of a pipeline segment there are a number of interrelated activities that must be performed.  The completion of each activity is essential to a successful inspection by ensuring that the proper inspection tools are utilized to address the known pipeline threats and required conditions are appropriately remediated.  These activities include, but are not limited to, pre-assessment data collection and analysis; pipeline preparation and retrofitting, application of appropriate inspection tools, post-assessment data verification and analysis, and remediation and repair work. The preparation and retrofitting of pipelines to accommodate in line inspection tools can be an extensive effort including the replacement of main line valves and fittings that are restrictive, and the installation of launchers and receivers. These complex projects have a significant impact on the capital component of pipeline inspections.

It should also be noted that, due to their scope and complexity, many integrity projects span multiple years and have both capital and O&M components depending on applicable accounting rules.  Accordingly, the project inspection costs will be applied over multiple years, with specific activity expenses applied during the year that the activity was performed.  However, the “completed mileage” of a project is accounted for in the year the project was finally completed.  These accounting differences must be considered if there are efforts to perform a correlation between annual recorded inspection costs and annual completed mileage totals.

The following table shows the inspected mileage completed per year with the associated expenses incurred in the year the work was performed.  The capital expenses shown are in thousands of fully loaded, nominal dollars.  The O&M expenses shown are in thousands of direct, nominal dollars.  Based on the accounting practices utilized, O&M expenses are managed at the program level and no differentiation between transmission and distribution expenditures is available.  The table below shows the complete annual O&M expenses.

Transmission Integrity Management Program

Miles Inspected of Transmission pipelines and Cost of Inspection1

(Thousands, nominal dollars)

|  | SoCalGas | SDG&E |
| --- | --- | --- |
| Calendar Year | Miles Inspected | Cost of Inspection | Miles Inspected | Cost of Inspection |
|  |  | Capital2 | O&M3,4,5 |  | Capital2 | O&M3,4,5 |
| 2003 | 100 | $13,415 | n/a | 0 | 0 | n/a |
| 2004 | 181 | $25,476 | n/a | 0 | 0 | n/a |
| 2005 | 282 | $33,471 | $5,205 | 2 | 0 | $499 |
| 2006 | 643 | $37,043 | $10,961 | 1 | 0 | $941 |
| 2007 | 263 | $39,146 | $13,150 | 86 | $343 | $2,085 |
| 2008 | 71 | $29,838 | $11,777 | 19 | $789 | $2,262 |
| 2009 | 191 | $38,366 | $14,295 | 0 | $-1 | $736 |
| 2010 | 529 | $43,198 | $22,583 | 32 | $221 | $1,076 |
| 2011 | 117 | $80,547 | $26,664 | 3 | $14,999 | $4,342 |

1 – Capital expenditures include the costs for activities as discussed in this response as they relate to inspection efforts on DOT-defined Transmission lines operated by our Transmission Operations organizations.   Accounting records are such that O&M costs include the costs of both inspection activities and any associated O&M repair efforts on both Distribution and Transmission organization-operated DOT-defined transmission lines.

2 – Capital in thousands, fully loaded, nominal dollars

3 – O&M in thousands, direct, nominal dollars

4 – The O&M expenses for the Transmission Integrity Management Program are managed on a programmatic basis.  There is no ability to separate O&M expenses by transmission and distribution pipelines.  The O&M expenses shown in the table above include the total O&M expenses for both transmission and distribution pipelines.

5 – As explained in response to DRA-PZS-2, Question 1(e), “Expenses for 2004 and earlier are not included, because the accounting practices in place during that time did not allow the Transmission Integrity Management Program values to be separated and reported.”

- For purposes of this response, “repairs” is defined to include the installation of repair bands/sleeves, mechanical surface grinding, and replacement of short lengths of pipe.  The smaller repairs are traditionally O&M expenses.  Occasionally, larger portions of pipe will be replaced in lieu of numerous, close-proximity, small repairs.  These larger repairs, or replacements, are capital expenses.  While SoCalGas and SDG&E can provide the number of repairs, the individual repair costs are incorporated with the other associated project costs within the work order (such as excavation costs, pipeline preparation and direct examination, and backfill and paving costs, etc.), and are not clearly identifiable.

The table below shows data for years 2003 through 2009 which indicate the number of individual repairs made on pipe segments.  Each repair, depending on type, could remove a single anomaly or multiple pipe anomalies depending on proximity to one another.  Beginning in 2010, due to regulatory reporting changes, SoCalGas and SDG&E began to track and report the number of anomalies removed rather than the number of repairs made.

Transmission Integrity Management Program

Transmission-Operated DOT-Defined Pipelines

Number of Pipeline Repairs Made on Inspected Miles

| Year | SoCalGas | SDG&E |
| --- | --- | --- |
| 2003 | 4 | 0 |
| 2004 | 5 | 0 |
| 2005 | 175 | 0 |
| 2006 | 36 | 0 |
| 2007 | 20 | 0 |
| 2008 | 9 | 0 |
| 2009 | 12 | 0 |
| 2010 | 80 | 0 |
| 2011 | 61 | 0 |

- See Response DRA-DAO-18-05(a) above.

- See Response DRA-DAO-18-05(b) above.

- The table below shows the SoCalGas transmission-operated DOT-defined pipeline footage replaced, the diameter of the pipe replaced, and the total annual charges to the associated work order.  Pipe replacement is typically one aspect in the scope of a job.  The costs specific to the replacement portion are not individually tracked, therefore, the total work order costs are shown.  The material used for all transmission pipeline replacements is steel.  Through the end of 2011, there have been no TIMP-related pipeline replacements at SDG&E.

Transmission Integrity Management Program

SCG Miles of Transmission-DOT Pipeline Replaced

(Thousands, nominal dollars)

- See Response DRA-DAO-18-05(e) above.

- See Response DRA-DAO-18-05(e) above.

QUESTION DRA-DAO-18-06:

Provide the following for SoCalGas’ and for SDG&E’s distribution pipelines for each year from 2001-2011:

  - The number of miles inspected.

  - The number of repairs made.

  - The expense incurred for inspection.

  - The expense incurred for repairs.

  - The number of miles of pipelines replaced.

  - The cost incurred for pipeline replacement.

  - A breakdown of the replacement cost of the lines replaced by segment, diameter, and pipeline material.

RESPONSE DRA-DAO-18-06

For purposes of preparing these responses, “transmission pipelines” is construed to refer to the United States Department of Transportation (DOT) defined transmission pipelines operated by SoCalGas and SDG&E’s Gas Distribution Operations organizations.

The Transmission Integrity Management Program was initiated in 2002 pursuant to federal regulations, with work commencing in 2003.  Because the program efforts did not start until 2003, responsive data on work elements and costs is not readily available before that time.  While no formalized TIMP-like inspection program was in place prior to 2003, SoCalGas and SDG&E have performed maintenance/inspection activities to validate the integrity of the transmission pipelines, including leak surveys, pipeline patrols, damage prevention programs and corrosion control measures, among others.  In addition, whenever pipeline segments are exposed, their condition and attributes are examined and recorded and any required remedial actions are addressed.

- To complete the inspection of a pipeline segment there are a number of interrelated activities that must be performed.  The completion of each activity is essential to a successful inspection by ensuring that the proper inspection tools are utilized to address the known pipeline threats and required conditions are appropriately remediated.  These activities include, but are not limited to, pre-assessment data collection and analysis; pipeline preparation and retrofitting, application of appropriate inspection tools, post-assessment data verification and analysis, and remediation and repair work.  The preparation and retrofitting of pipelines to accommodate in line inspection tools can be an extensive effort including the replacement of main line valves and fittings that are restrictive, and the installation of launchers and receivers. These complex projects have a significant impact on the capital component of pipeline inspections.

It should also be noted that, due to their scope and complexity, many integrity projects span multiple years and have both capital and O&M components depending on applicable accounting rules.  Accordingly, the project inspection costs will be applied over multiple years, with specific activity expenses applied during the year that the activity was performed.  However, the “completed mileage” of a project is accounted for in the year the project was finally completed.  These accounting differences must be considered if there are efforts to perform a correlation between annual recorded inspection costs and annual completed mileage totals.

The following table shows the inspected mileage completed per year with the associated expenses incurred in the year the work was performed.  The capital expenses shown are in thousands of fully loaded, nominal dollars.  The O&M expenses for DOT- distribution pipelines are included in the table in response to Question 5(a).  Based on the accounting practices utilized, O&M expenses are managed at the program level and no differentiation between transmission and distribution expenditures is available.

Transmission Integrity Management Program

Miles Inspected of Distribution Organization-Operated DOT-Defined Transmission Pipelines and Cost of Inspection1

(Thousands, nominal dollars)

|  | SoCalGas | SDG&E |
| --- | --- | --- |
| Calendar Year | Miles Inspected | Cost of Inspection | Miles Inspected | Cost of Inspection |
|  |  | Capital2 | O&M3 |  | Capital2 | O&M3 |
| 2003 | 0 | $5 | -- | 0 | 0 | -- |
| 2004 | 0 | $2,266 | -- | 0 | 0 | -- |
| 2005 | 0 | $2,089 | -- | 0 | 0 | -- |
| 2006 | 4 | $185 | -- | 0 | 0 | -- |
| 2007 | 61 | $3,751 | -- | 0 | 0 | -- |
| 2008 | 43 | $369 | -- | 12 | 0 | -- |
| 2009 | 17 | $4,428 | -- | 10 | 0 | -- |
| 2010 | 23 | $23,365 | -- | 3 | $1,622 | -- |
| 2011 | 33 | $25,220 | -- | 22 | $1,431 | -- |

1 – Capital expenditures include the costs for activities as discussed in this response as they relate to inspection efforts on DOT-defined Transmission lines operated by our Transmission Operations organizations.   Accounting records are such that O&M costs include the costs of both inspection activities and any associated O&M repair efforts on both Distribution and Transmission organization-operated DOT-defined transmission lines.

2 – Capital in thousands, fully loaded, nominal dollars

3 - The O&M expenses for the Transmission Integrity Management Program are managed on a programmatic basis.  There is no ability to separate O&M expenses by transmission and distribution pipelines.  The O&M expenses shown in the table in response to Question 5(a) include the total O&M expenses for both transmission and distribution pipelines.

- For purposes of this response, “repairs” is defined to include the installation of repair bands/sleeves, mechanical surface grinding, and replacement of short lengths of pipe.  The smaller repairs are traditionally O&M expenses.  Occasionally, larger portions of pipe are replaced in lieu of numerous, close-proximity, small repairs.  These larger repairs, or replacements, are capital expenses.  While SoCalGas and SDG&E can provide the number of repairs, the individual repair costs are incorporated with the other associated project costs within the work order (such as excavation costs, pipeline preparation and direct examination, and backfill and paving costs, etc.), and are not clearly identifiable.

The table below shows data for years 2003 through 2009 which indicate the number of individual repairs made on pipe segments.  Each repair, depending on type, could remove a single anomaly or multiple pipe anomalies depending on proximity to one another.  Beginning in 2010, due to regulatory reporting changes, SoCalGas and SDG&E began to track and report the number of anomalies removed rather than the number of repairs made.

Transmission Integrity Management Program

Distribution Organization-Operated DOT-Defined Transmission Pipelines

Number of Pipeline Repairs Made on Inspected Miles

| Year | SoCalGas | SDG&E |
| --- | --- | --- |
| 2003 | 0 | 0 |
| 2004 | 0 | 0 |
| 2005 | 0 | 0 |
| 2006 | 4 | 0 |
| 2007 | 18 | 0 |
| 2008 | 1 | 3 |
| 2009 | 1 | 0 |
| 2010 | 4 | 0 |
| 2011 | 26 | 4 |

- See Response DRA-DAO-18-06(a) above.

- See Response DRA-DAO-18-06(b) above.

- The table below shows the SoCalGas Distribution Operations organization-operated DOT-defined transmission pipeline footage replaced, diameter and associated replacement cost of the work order.  The costs specific to the replacement portion are not individually tracked, therefore the total work order costs are shown. Through the end of 2011, there have been no TIMP-related pipeline replacements at SDG&E.  All replacements are steel.

Transmission Integrity Management Program

SCG Miles of Distribution-DOT Pipeline Replaced

(Thousands, nominal dollars)

- See Response DRA-DAO-18-06e) above.

- See Response DRA-DAO-18-06(e) above.

QUESTION DRA-DAO-18-7:

On page WP-IX-1-6, SoCalGas estimates that an average of one repair would be needed for each pressure test segment.  SoCalGas provided the following explanation for this estimate in its response to DRA’s data request DRA-DAO-06, question 3:

“Given the short timeframe allotted for preparation of the PSEP, subject matter expertise was relied upon to determine the scope and estimated cost associated with post-pressure test repair work.  A specific set of projects was not consulted, but rather institutional knowledge of previous repair work was applied to determine a reasonable, high level allowance to include as part of the total cost of the pressure testing effort.  Every project contains unique circumstances that can affect both scope and cost.”

- Please provide a copy of any and all materials, including any and all procedures, relied on by Sempra’s subject matter experts as referenced above.

- Please provide the name of all “subject matter experts” referenced in the response, and identify their job title, job description, and the number of years of experience at Sempra.

- Please provide a walk-through of how Sempra’s’ subject matter experts used the materials and/or procedures identified in 6(a) above to determine that 1 repair would be needed for each pressure test segment.

- Did Sempra perform any analyses and or assessments on any of its pipelines to determine that repairs would be needed once a pressure test was performed on the pipeline?  If yes, please provide a copy of any and all analyses and assessments.

- Did Sempra rely on industry experience to determine that repairs would be needed once a pressure test was performed on a pipeline?  If yes, please provide a copy of all literature and or studies relied on for this determination.

RESPONSE DRA-DAO-18-7:

- As indicated in the Response to DRA-DAO-06-1, the allowance for post-pressure test repairs was based on engineering and construction judgment.  No specific studies, analyses, or procedures were prepared in developing these allowances.

- The input of the many knowledgeable personnel working in SoCalGas and SDG&E operations was considered when developing the assumptions and approaches outlined in the PSEP, including the high level assumption, for purposes of capturing repair costs, of one repair per pressure test segment.  The following company personnel are among the most experienced in the areas of pressure testing and pipe installation activities:

  - Roger Warr, Manager of Project and Construction Management group, 32 years of experience at SoCalGas

  - Ron Bott, Project Manager III, 38 years of experience at SoCalGas

  - Alan Ahern, Gas Transmission Operations Manager, 39 years of experience at SoCalGas

- The estimated pressure test repair cost included in the Pipeline Safety Enhancement Plan is intended to be a high level allowance to cover post-pressure test repair work that may be necessary on a given project.  The assumption of one repair per pressure test segment was used as the basis for developing the cost estimate.  This does not suggest any level of certainty that one repair will be needed per pressure test segment.  Each project will be unique and may require zero, one, or multiple repairs per pressure test segment.  The nature of the repair (pin-hole leak versus a rupture) and the location (rural versus urban) can dramatically influence the cost of a repair.

- As explained on page 56 of the Testimony:

“While SoCalGas and SDG&E are confident in the safety of their pipeline system, pressure testing will expose pipelines to pressure levels well in excess of pressures typically experienced in-service.”

Consequently, small leaks or other failures may occur, and the estimated pressure testing costs include an allowance for repairing such failures.

Segment-specific analyses and assessments were not performed on the pipelines proposed to be pressure tested in the PSEP to determine whether any flaws exist that will fail under the pressure anticipated to be achieved during the test.  In the PSEP, SoCalGas and SDG&E propose to perform an in-line-inspection assessment using a TFI tool on piggable pipelines before the pressure testing is done.  As explained on page 57 of the Testimony:

“knowledge obtained through in-line inspection using a TFI tool can be used to facilitate proactive mitigation of any pipeline anomalies that may lead to a potential pipeline failure at higher pressure test levels.”

- Pipeline failures during the execution of a pressure test have been experienced by other operators in the oil and gas industry.

A report put together by AGA addresses this issue, stating:

“A failed pressure test may result in an unplanned pipeline or system outage.  If unanticipated pressure test failures occur, the line may remain out of service longer than originally planned in order to make necessary repairs and complete the pressure test successfully.”

PG&E also experienced pressure test failures on some of the projects executed in 2011 as part of its PSEP effort.  Pressure testing of existing gas transmission pipelines, some that are over 60 years old, on such a wide scale, as is required by the CPUC, has never before been completed.  Thus, reliable industry metrics on pressure testing costs and repairs is not available.

QUESTION DRA-DAO-18-8:

In response to DRA-DAO-7, question 1, in which DRA asked SoCalGas to identify the criteria used to determine whether a segment can be taken out of service in the Decision Tree, SoCalGas stated:  “…The criteria used to determine whether a segment can be taken out of service varies based upon specific pipeline and local system characteristics that may include, but are not limited to system looping and flexibility; impact to capacity; curtailment to non-core customers; impact to shippers, customers, and the gas market; availability of alternative sources of gas; anticipated outage duration; and the ability to mitigate these negative impacts through construction of parallel systems.”

Please answer the following questions regarding SoCalGas’ response above:

- For each line that is planned for replacement in the PSEP, please identify the criteria used to determine that it cannot be taken out of service.

- For each line that is planned for replacement in the PSEP, please explain if the segments identified within the line have ever been taken out of service for maintenance, repair, or replacement.

- For each line that is planned for replacement in the PSEP, please explain how SoCalGas was able to take the affected segments out of service for maintenance, repairs, or replacement, in the past.

- For each line that is planned for replacement in the PSEP, please explain why these affected lines cannot now be taken out of service for pressure testing.

RESPONSE DRA-DAO-18-8:

- For the purposes of PSEP estimates, a 2-6 week outage window was used as the baseline assumption for determination of whether or not a pipeline system could be removed from service. As referenced previously in data response DRA-PZS-07 response 8, the information provided to date represents best estimates by the operations personnel most knowledgeable of the SoCalGas/SDG&E systems, and their general understanding of the flexibility available to remove a pipeline from service for pressure testing (considering factors such as the number of customers, customer gas loads, availability of secondary feeds, etc.).  As such, line by line detail of the specific factors preventing removal from service is not available at this time.  These estimates were generated for the purpose of further defining a scope and associated costs, and changes to these estimates will not be known until the projects are engineered at the detailed level.

- It is not possible to readily identify the segment by segment specific history of removal from service for maintenance, repair, or replacement purposes  Typically repairs are performed at reduced pressures to avoid service disruption or localized temporary bypass pipe is installed around the area to be repaired when removal from service is required.  When pipelines need to be taken out of service for maintenance, the work is scheduled at times when demand is low and the duration is typically no more than 48 hours.

- It is not possible to readily identify how every pipeline has been removed from service on a pipeline by pipeline basis for all pipelines contained within the PSEP.

The ability to remove a pipeline from service is dependent upon a combination of several variables related to the system characteristics previously mentioned as part of Response DRA-DAO-7-1.  Routine pipeline maintenance and repair activities can often be performed while the pipeline remains in service, or with minimal or short duration impact.  These routine maintenance and repair activities are expressly different in timing and scope compared to the logistics and circumstances involved with pipeline pressure testing and replacement planning.

- Planning provided as part of the PSEP is based on broad assumptions for the purposes generating high level estimates.  Segment-specific detail will be generated during the follow-on detailed planning phases of work.   Please refer to DRA-DAO-18-08c.

# Footnotes

AGA - Summary of Costs and Factors Impacting In-Line Inspection, Direct Assessment, Pressure Testing and Pipeline Replacements For Natural Gas Transmission Pipelines - April 4, 2011